Portable Solar Power Inverter LG-6000A2-C

User Manual

1 . Product  description

The  LG  Series are lightweight, portable and  beautiful  with  large  capacity  lithium  electricity  which  surpassing  other  product  in  the  world.  The  products  use  progressive  lithium battery  workmanship. Outputting  powerful  energy  providing  two  types  different  voltage  mode  AC/DC. For  adaptive  different  electronic  products  demand. The  product  can  use  as  on-line UPS or  pre-emergency  standby  power. Meeting  power  requirements  of  most  mobile  electronic  products.

The product include many lithium battery. The total capacity  can  provide outpouring .when the  power cut ,the product can provide traditional desktop model at home for 3~24 hours under starting up circumstances. At the same time ,can use for indoor or outdoor standby or meet an emergency power and other application. 220V/12V/5V DC/AC outputting can be suitable for different equipments, just like mobile phone, tablet PC, laptop, small printer, some kinds lanterns, fish tank heater, photographic, electrombile ,medical treatment equipments and so on .Our product abandon some weakness from traditional UPS power.it is necessary for traveling, outdoor working, camping out and mountaineering risk.

2. Function introduction and instruction

1.Product connection diagram

2,Detail of LCD

1 Input Voltage   2 Working Mode   3 Output Voltage

4 Solar Panel     5 Battery Status   6 Loading Application

7 Silent Mode    8 Loading Status

3,Detail of indicate lamp & button

| INPUT | AC input voltage |
| --- | --- |
| Hz | output frequency / Working mode |
| OUTPUT | AC output voltage |
| BATT. CAPACITY | Battery working condition and capacity |
| LOAD | Load power |
| NORMAL | AC input at normal status |
| FAULT | False signal light |
| BATTERY | Battery mode |
| 25%--100% | Overload condition |
|  | ENTER |
|  | ON/OFF |
|  | UP |
|  | DOWN |

4. Function and setting

ON/OFF Button: Press for 3 seconds to turn on and 5 seconds turn off.

ENTER Button: Press for 5 seconds start to set Mode P0 to P4. PROitch through UP & DOWN button.

Mode P0- Pre-set. Press ENTER 2 times to end up setting. Auto Exit after 10 seconds' no-ops.

Mode P1- Power supply setting. 01- AC supply in priority, 02- Energy saving. 03- Battery supply in priority, PROitch through UP & DOWN and select through ENTER button.

| Position | Float(V) | Position | Float(V) |
| --- | --- | --- | --- |
| U0=Gel U.S.A | 13.7V | U4=Gel European | 13.8V |
| U1=A.G .M.1 | 13.4V | U5=Open lead acid | 13.8V |
| U2=A.G .M.2 | 13.7V | U6=Calcium (open) | 13.6V |
| U3=Sealed lead Acid | 13.6V |  |  |

Mode P2- Battery Type setting. PROitch through UP & DOWN and select battery type through ENTER button.

Mode P3- Charging Current 0-35A selecting. 0-20%-40%-60%-80%-100%, Maximum is 35A, Minimum 0A.

Mode P4- Voice setting. PROitch the Buzzer through UP & DOWN and select through ENTER button.

5. Connection

Attention:

Terminal and output plug are both available to connect the load. Output plug can only allow the loading under 1500W. Loading over 1500W should connect to terminal.

Solar wiring diagram

Note：

If connect to generator, must follow the steps below：

- Start generator, after it go stably, connect its output port to inverter’s input port (to be sure there isn’t any load connecting to inverter at this moment).

- Start the inverter, connect the loads one by one.

- Choose generator with 2 or 3 times capacity compared to inverter.

- Solar inverter’s panel and connection is different from common model.

- The voltage of solar panel should follow the Technical parameter.

Back panel connection

| BATTERY Negative | Battery negative polarity connection |
| --- | --- |
| BATTERY Positive | Battery positive polarity connection |
| AC INPUT | AC input connection |
| AC OUTPUT | Universal socket output or terminal output |
| FUSE AC INPUT | Ac input voltage over current protection |
| FUSE AC OUTPUT | Ac output voltage over current protection |

Note：

If connect to generator, must follow the steps below：

- Start generator, after it go stably, connect its output port to inverter’s input port (to be sure there isn’t any load connecting to inverter at this moment).

- Start the inverter, connect the loads one by one.

- Choose generator with 2 or 3 times capacity compared to inverter.

- Solar inverter’s panel and connection is different from common model.

- The voltage of solar panel should follow the Technical parameter.

6. Care and maintenance

●This series of inverter fairly needs maintenance. Turn to battery charge mode to extend the life of battery.

●discharge and charge the batteries at least 1 time every 6 months. Charging time should not be less than 12 hours.

●In high temperature area, battery should be charged and discharged every 2 months and standard charging time is not less than 12 hours.

●Basically batteries works 3-5 years, should replace when working not well.

●Ask professionals to replace the batteries

Note：

- Before replacing battery, must PROitch off battery, inverter and mains supply.

- Put off the metal object like ring, watch etc.

- Use insulated tool and avoid putting any tool and metal object on battery.

- When connecting battery, it may strike some unharmful sparks.

- Do not make converse connection.

7. Solution for difficult situation

| False | Cause | Solution |
| --- | --- | --- |
| No city power input | Recoverable fuse popup | Press fuse back |
| Terminal heating | Fault or loose connection | Reconnect |
| Auto PROitch off with loads | Battery no power or overload | Charge battery or reduce loads |
| PROitch on failure | Fault connection with city power or battery | Check connection with battery or reconnect |
| Alarm when PROitch on | Battery no energy or overload | Charge battery or reduce loads |
| Buzzer screams 2 secs every 3 secs | Over temperature alarm (85℃-alarm，90℃-shut down) | Check if fan or vents jammed |
| Fan’s speed not stable | Smart control according to temperature | Leave it |

8.Technical parameter

| MODEL |  | LG2000 | LG3000 | LG5000 | LG6000 |
| --- | --- | --- | --- | --- | --- |
| RATED CAPACITY |  | 1600w | 2400W | 4000w | 4800W |
| INPUT | VOLTAGE | (165-265)VAC |  |  |  |
|  | FREQUENCY | 45-65HZ |  |  |  |
| OUTPUT | VOLTAGE | 220V/±2%（BATTERY MODE） |  |  |  |
|  | FREQUENCY | 50/60HZ±1%（BATTERY MODE） |  |  |  |
| OUTPUT WAVEFORM |  | PURE SINEWAVE |  |  |  |
| EFFICIENCY |  | ＞85% |  |  |  |
| BATTERY |  | The lithium battery |  |  |  |
| BATTERY RATED VOLTAGE |  | 24VDC |  | 48VDC |  |
| MAX AC CHARGING CURRENT |  | 10A(OPTIONAL) |  |  |  |
| SOLAR INPUT VOLTAGE |  | 48-150V |  |  |  |
| SOLAR CHARGE CURRENT |  | 30A 60A |  |  |  |
| PROTECT |  | OVERLOAD,SHORT CIRCUIT,BATTERY HIGH AND LOW VOLTAGE AND AC INPUT HIGH AND LOW VOLTAGE PROTECTION |  |  |  |
| TRANSFER TIME |  | ≤6MS |  |  |  |
| CAPACITY OF OVERLOAD |  | 110-125% TURN TO BYPASS AFTER 60 SECS,150%MAINTAIN 10S AND THEN SHUT DOWN |  |  |  |
| COMMUNICATION PORT |  | RS-232/USB(OPTIONAL) |  |  |  |
| OPERATING ENVIROMENT | TEMPERATURE | -40~55℃ |  |  |  |
|  | HUMIDITY | 10%-90% |  |  |  |
| CASE SIZE:L*W*H(mm) |  | 478*313*688mm |  |  |  |
| PACKAGE SIZE:L*W*H(mm) |  | 530*430*720mm |  |  |  |
| N.W/G.W(kg) |  |  |  | 51/56 |  |